## Instructions
Closed loop water treatment log
One row per parameter per sample. Every row should read correctly on its own.
Before the visit
1. For each loop and parameter, write the Reference range and its Range source (document and year) before any result exists.
2. Keep those ranges unchanged for the round. A range changed after a result is seen starts a new round.
3. Record the fill baseline once: a sample taken soon after start-up and kept for the life of the fluid, with its laboratory values.
At the sample point
4. Sample well-mixed, circulating fluid. Do not sample expansion tanks, reservoirs, low-point drains or dead legs. Flush the port first.
5. Wear the protection named in section 8 of the fluid's safety data sheet. Hot or pressurized loops follow the site permit procedure.
6. Label each bottle with date, loop and location. Use the same names at every visit.
Recording
7. Enter the Result with its Unit and the Method or kit actually used (meter, kit name and lot, or laboratory method).
8. In range: Y = inside the range; N = outside; T = inside the range but moved away from the loop's own baseline.
9. For N or T, write the Action taken and who was told. A laboratory result is entered as its own row with the laboratory method.
10. Read the makeup water meter and enter the litres added since the last visit.
Where ranges come from
Use the range of the fluid actually in the loop, from the fluid or inhibitor supplier or the site water treatment specification.
BS 8552:2012 (BSI code of practice for sampling closed systems) gives no action levels; published guides give ranges only under their own conditions.
Published examples, with their conditions, are listed in the article at the address in the footer. Do not copy them for a different fluid.
Limits
This log is for sealed heating, chilled water and glycol loops sampled at visits. It is not for open cooling towers, steam boilers or sprinkler systems.
It records indicators, not a corrosion rate. Dissolved oxygen needs inline measurement; corrosion rate needs coupons or a corrosion monitor.
It is evidence for the water treatment specialist, not a laboratory report and not a treatment decision.
Sheets
Log: the blank log. Example: an illustrative filled log; its values come from no real site.
A CSV file with the Log header row is supplied for tools that import CSV but not xlsx.

## Log
Date and time (YYYY-MM-DD hh:mm) | Loop ID | Fluid (water only, or glycol type, target %, product) | Sample point (after flushing) | Parameter | Method or kit (and lot) | Unit | Reference range (in Unit) | Range source (document, year) | Result (in Unit) | In range (Y/N/T) | Action taken (what, who was told) | Retest result (value, date) | Makeup since last visit (L) | Tested by

## Example
ILLUSTRATIVE EXAMPLE. All values are invented to show how rows are filled; they come from no real site and are not targets.
Date and time (YYYY-MM-DD hh:mm) | Loop ID | Fluid (water only, or glycol type, target %, product) | Sample point (after flushing) | Parameter | Method or kit (and lot) | Unit | Reference range (in Unit) | Range source (document, year) | Result (in Unit) | In range (Y/N/T) | Action taken (what, who was told) | Retest result (value, date) | Makeup since last visit (L) | Tested by
2026-11-04 09:30 | CHW-02 | Inhibited PG, 30 % target | Return header sample valve | pH | Handheld pH meter, calibrated at 4, 7, 10 | pH units | 8.0 to 10.0 | Fluid supplier guide, 2008 | 7.6 | N | Fluid supplier told; lab sample sent | 7.7 on 2026-11-11 | 120 | Technician A
2026-11-04 09:35 | CHW-02 | Inhibited PG, 30 % target | Return header sample valve | Glycol | Refractometer, PG scale | vol % | 27 to 33 | Site specification, 2025 | 29 | Y | None |  | 120 | Technician A
2026-11-04 09:40 | CHW-02 | Inhibited PG, 30 % target | Return header sample valve | Conductivity | Handheld meter | µS/cm | 1,000 to 10,000 (formulation range) | Fluid supplier data sheet, 2025 | 3,100 | T | Up 29 % on fill baseline 2,400; trend flagged to treatment specialist |  | 120 | Technician A
2026-11-18 (report date) | CHW-02 | Inhibited PG, 30 % target | Return header sample valve | Copper | Laboratory, ICP | ppm | Below 3 | Fluid supplier specification, 2025 | 0.4 | Y | Lab report ref. L-0001 filed |  |  | Laboratory